GW TEST – SUPERVISOR SW INSTRUCTION MANUAL

Rev. 03

MAIN MENU

The main menu is divided in three sections:

- Test management

- System management

- Allarms

1

2

3

Other functions:

- Program database upload (event list, operator list, email addresses)

- Save the program database (event list, operator list, email addresses)

- Management of the program configuration

- Event list

- Instruction manuals

- TEST MANAGEMENT

1A) RESTART TEST

By this function it is possible to launch the automatic RCCB test for all the devices on the bus (only for devices with autotest function).

The program can manage only the device with the autotest function.

The program shows the RCCB test result:

The RCCB test is OK.

The RCCB test is KO. Call an electrical technician to solve the problem.

No response from the device (the device is not connected to the bus system or it is not powered).

If a device result is without any symbol it means that the connected device do not have autotest function inside.

At the end of the RCCB test it is showed the result for all the connected device

and it is created an excel file with the results.

1B) FUNCTIONAL TEST

In case Nemodin are included in the plant, is possible to run the functional test on all lamps, or, if you press “No” in the window below, all results of the last functional test performed on each lamp will be shown. A maximum time of 6 minutes could be necessary to perform the test.

1C) BATTERY TEST

In case Nemodin are included in the plant, is possible to run the battery test on all lamps, or, if you press “No” in the window below, all results of the last battery test performed on each lamp will be shown. A maximum time of 6 hours could be necessary to perform the test.

1D) TEST ARCHIVE

It opens the folder where there are the result of the previous RCCB tests.

- PLANT MANAGEMENT

GWTEST allows to command and to monitor the status of the connected devices:

- the RCD status is displayed (lever ON, lever OFF, trip for short circuit or earth leakage current fault)

- the Restart Autotest status is displayed (insulation system check, autotest)

- to open/close the RCCB from remote position (only Restart/Autotest devices)

- to lauch autotest function for every RCCB or RCCB cluster

- auxiliary contact status is displayed

- to configure the auxiliary contact status

For emergency lamps you can:

- See the type of lamp (emergency lamp autonomous, Emergency Kit, lamp Node)

- View the lamp status (Normal, Emergency, test in progress, Inhibition, Low Power, Spare, not set) and if the lamp is in Permanente (on) status or not permanent (off)

- View alarms of the lamp (Test not run, battery failure, battery not connected, battery KO, tube KO, sync Alarm, LON Communication alarm)

- Show dates and results of the last functional and battery test

- Send command of Permanent (switch on), not Permanent (off), functional test or battery, Spare, Reset and Wink)

2A)  STRUCTURE OF THE SYSTEM

The devices are shown by tree structure on the left part of the screen (Places of installation →boards→devices/lines). A color caption is used to simplify the research of possible faults or anomaly in the lines/devices.

Below the color caption shown in order of priority:

YELLOW = Alarm of Restart Autotest device anomaly, to call a technician

RED = System fault alarm (blocked status, waiting status for low insulation), alarm for BUS line communication problem, alarm for problem in the connection between BUS module and Restart Autotest.

LIGHT GRAY = Autotest or restart function in progress

DARK GRAY = Deactivated device, the autotest and restart functions are deactivated (slide cover to the right)

GREEN = Activated device (slide cover to the left)

The status and commands available for the selected device (or cluster of devices) are shown on the left part of the screen.

RCD lever status (ON, OFF) and device status (RCCB self test in progress, anomaly of the device, check of the system in progress, trip for earth leakage current fault, trip for short circuit fault, ecc…).

Device technical data of Restart.

Command to send to the device (opening and reclosing command, RCCB autotest , reclosing command previous check of the system).

Result of the last executed restart/autotest and relative counter.

Visualisation of the last events regarding the selected device.

By pushing the following button it is possible to obtain additional data.

Auxiliary contact setting.

Notification of device alarm status.

By selecting a site or a board in the system tree which it contains more Restart Austotest devices, it is possible to launch the autotest  for all the selected devices.

2B)  DEVICE STATUS

It is visualized the status of all the Restart and Emergency Lamps connected to the bus system.

It is possible instantaneusly to see the following data:

- circuit breaker ON/OFF (in case of a Restart)

- device status (Autotest anomaly, short circuit, low insulation, ecc…)

- Installation site of the device

- Device and protected line

- Device code

- Result and date regarding the last executed test

- Date of the last executed restart

It is used the same color caption used in “STRUCTURE OF THE SYSTEM”.

2C)  PLANIMETRIES

The management by planimetry is enabled only if it is selected during the phase of  GwTest software installation/ configuration.

The devices on the planimetry are highlighted by different color using the same color caption of “STRUCTURE OF THE SYSTEM”.

- ALARMS

Alarms are shown in the specific section.

The operator that he takes in charge the alarm has to tick the warning, so the other operators will see the name of the operator involved and the date of the tick. Eventual emails of that alarm will never be sent.

Alarms will automatically disappear when the problem will be solved.

- UPLOAD EXISTING FILE

Upload the past configuration.

- SAVE

Save the current configuration.

- PROGRAM SETTING

There are tree typology of settings.

- Gestione operatori – Operator management

The administrator has to enable the functions of the other operators during the configuration of the software (administrator, power user, user). It is also possible to add, to modify, to cancel an operator.

- Report Excel configuration

The field of the excel autotest report can be modified.

- Notifications/alarms

To use email for sending alarms it is important to create a recipient list and to set the type of alarm.

The time referring to "Send alarm every" is the time interval in which emails containing new alarms occurred in the system are sent. For example, setting "1 hour", would be sent all the reports occurring in the course of an hour in a single email.

If nobody solve the cause of the alarm, the sending of the mail will be repeated every setted time.

- EVENT LIST

By “event list” button it is possible to see all events regarding the connected devices.

It is possible to print or to save the event list in excel format.

The “Delete” command will definitely cancel the shown events from the database.

- INSTRUCTION MANUAL

This command allows to see the instruction manual.